## PV
Group | Unit | Scale | Description | Adress | Document Address | RW | Length | Type | Memo
Status |  |  | 장치 번호 | 100 | 40101 | R | 1 | unsigned
|  |  | 사이트 번호 | 101 | 40102 | R | 1 | unsigned
|  |  | 지역번호 (RCC) | 102 | 40103 | R | 1 | unsigned
|  |  | 제주도 여부 (1 : TRUE, 0 : FALSE) | 103 | 40104 | R | 1 | unsigned
REALTIME | kW | 10 | 유효출력 | 104 | 40105 | R | 1 | signed
| kVar | 10 | 무효출력 | 105 | 40106 | R | 1 | signed
| kW | 10 | 역방향 유효출력 | 106 | 40107 | R | 1 | signed
| kVar | 10 | 역발향 무효출력 | 107 | 40108 | R | 1 | signed
voltage | V | 10 | voltage R | 108 | 40109 | R | 1 | signed
| V | 10 | voltage S | 109 | 40110 | R | 1 | signed
| V | 10 | voltage T | 110 | 40111 | R | 1 | signed
current | A | 100 | current R | 111 | 40112 | R | 1 | signed
| A | 100 | current S | 112 | 40113 | R | 1 | signed
| A | 100 | current T | 113 | 40114 | R | 1 | signed
| Hz | 100 | 주파수 | 114 | 40115 | R | 1 | unsigned
누적값 |  | 10 | 총 유효출력 누적값 | 115 | 40116 | R | 2 | signed
|  | 10 | 일일 유효출력 누적값 | 117 | 40118 | R | 2 | signed
|  | 10 | 총 무효출력 누적값 | 119 | 40120 | R | 2 | signed
|  | 10 | 총 역방향 유효출력 누적값 | 121 | 40122 | R | 2 | signed

## PCS
Group | Unit | Scale | Description | Adress | Document Address | RW | Length | Type | Memo
Status |  |  | Command Result | 1000 | 41001 | R | 1 | unsigned
|  |  | 시퀀스 번호 | 1001 | 41002 | R | 1 | unsigned
|  |  | Pcs Version | 1002 | 41003 | R | 1 | unsigned | 충전: 음수 방전: 양수
|  |  | Mode | 1003 | 41004 | R | 1 | unsigned
|  |  | Remote Enable | 1004 | 41005 | R | 1 | unsigned | 설정 확인용
|  |  | AcMagnet Close | 1005 | 41006 | R | 1 | unsigned
|  |  | DcMagnet Close | 1006 | 41007 | R | 1 | unsigned
|  |  | 충전 횟수 | 1007 | 41008 | R | 1 | unsigned
|  |  | 방전 횟수 | 1008 | 41009 | R | 1 | unsigned
|  |  | GridStsStatus | 1009 | 41010 | R | 1 | unsigned
|  |  | DgStsStatus | 1010 | 41011 | R | 1 | unsigned
|  |  | HeartBeat | 1011 | 41012 | R | 1 | unsigned
|  |  | 상태 | 1012 | 41013 | R | 2 | unsigned
Fault |  |  | CommFault | 1014 | 41015 | R | 2 | unsigned
|  |  | Fault1 | 1016 | 41017 | R | 2 | unsigned
|  |  | Fault2 | 1018 | 41019 | R | 2 | unsigned
|  |  | Fault3 | 1020 | 41021 | R | 2 | unsigned
|  |  | Fault4 | 1022 | 41023 | R | 2 | unsigned
|  |  | Fault5 | 1024 | 41025 | R | 2 | unsigned
|  |  | Fault6 | 1026 | 41027 | R | 2 | unsigned
Warning |  |  | Warning1 | 1028 | 41029 | R | 2 | unsigned
|  |  | Warning2 | 1030 | 41031 | R | 2 | unsigned
Analog | Hz | 100 | 주파수 | 1032 | 41033 | R | 1 | signed
| kW | 10 | 유효출력 | 1033 | 41034 | R | 1 | signed
| kVar | 10 | 무효출력 | 1034 | 41035 | R | 1 | signed
| % | 10 | 역률 | 1035 | 41036 | R | 1 | signed
|  | 10 | Crate | 1036 | 41037 | R | 1 | signed
|  | 10 | Prate | 1037 | 41038 | R | 1 | signed
|  | 10 | 명령 Feedback | 1038 | 41039 | R | 1 | signed
| % | 10 | SOC 상한 | 1039 | 41040 | R | 1 | signed
| % | 10 | SOC 하한 | 1040 | 41041 | R | 1 | signed
| ℃ | 10 | Temp1 | 1041 | 41042 | R | 1 | signed
| ℃ | 10 | Temp2 | 1042 | 41043 | R | 1 | signed
| ℃ | 10 | Temp3 | 1043 | 41044 | R | 1 | signed
| ℃ | 10 | Temp4 | 1044 | 41045 | R | 1 | signed
|  | 10 | 누적 충전량 | 1045 | 41046 | R | 1 | signed
|  | 10 | 누적 방전량 | 1046 | 41047 | R | 1 | signed
| V | 10 | AC R-S 선간 전압 | 1047 | 41048 | R | 1 | signed
| V | 10 | AC S-T 선간 전압 | 1048 | 41049 | R | 1 | signed
| V | 10 | AC T-R 선간 전압 | 1049 | 41050 | R | 1 | signed
| V | 10 | AC R상 전압 | 1050 | 41051 | R | 1 | signed
| V | 10 | AC S상 전압 | 1051 | 41052 | R | 1 | signed
| V | 10 | AC T상 전압 | 1052 | 41053 | R | 1 | signed
| A | 100 | AC R상 전류 | 1053 | 41054 | R | 1 | signed
| A | 100 | AC S상 전류 | 1054 | 41055 | R | 1 | signed
| A | 100 | AC T상 전류 | 1055 | 41056 | R | 1 | signed
| V | 10 | DC 링크 전압 | 1056 | 41057 | R | 1 | signed
| V | 10 | DC 배터리 전압 | 1057 | 41058 | R | 1 | signed
| A | 100 | DC 배터리 전류 | 1058 | 41059 | R | 1 | signed
| V | 10 | DC 배터리 전력 | 1059 | 41060 | R | 1 | signed
| V | 10 | PCS단 R상 전압 | 1060 | 41061 | R | 1 | signed
| V | 10 | PCS단 S상 전압 | 1061 | 41062 | R | 1 | signed
| V | 10 | PCS단 T상 전압 | 1062 | 41063 | R | 1 | signed
|  |  | Operation Avaliable | 1063 | 41064 | R | 1 | signed
|  |  | Reserved | 1064 | 41065 | R | 2 | signed
제어 |  |  | 명령 | 1200 | 41201 | W | 1 | unsigned
| kW | 10 | 레퍼런스값 | 1201 | 41202 | W | 1 | unsigned
| % | 10 | SOC 상한 | 1202 | 41203 | W | 1 | unsigned
| % | 10 | SOC 하한 | 1203 | 41204 | W | 1 | unsigned

## BSC
Group | Unit | Scale | Description | Adress | Document Address | RW | Length | Type | Memo
Status |  |  | BSC Version | 2000 | 42001 | R | 1 | unsigned
|  |  | Rack Count | 2001 | 42002 | R | 1 | unsigned
|  |  | 상태 | 2002 | 42003 | R | 1 | unsigned
|  |  | MaxCellVoltageLocation | 2003 | 42004 | R | 1 | unsigned
|  |  | MinCellVoltageLocation | 2004 | 42005 | R | 1 | unsigned
|  |  | MaxModuleTempLocation | 2005 | 42006 | R | 1 | unsigned
|  |  | MinModuleTempLocation | 2006 | 42007 | R | 1 | unsigned
|  |  | HeartBeat | 2007 | 42008 | R | 1 | unsigned
|  |  | OnlineStatus1 | 2008 | 42009 | R | 1 | unsigned
|  |  | OnlineStatus2 | 2009 | 42010 | R | 1 | unsigned
|  |  | FanStatus1 | 2010 | 42011 | R | 1 | unsigned
|  |  | FanStatus2 | 2011 | 42012 | R | 1 | unsigned
Fault & Warning |  |  | Rack Warning Status1 | 2012 | 42013 | R | 1 | unsigned
|  |  | Rack Warning Status2 | 2013 | 42014 | R | 1 | unsigned
|  |  | Rack Fault Status1 | 2014 | 42015 | R | 1 | unsigned
|  |  | Rack Fault Status2 | 2015 | 42016 | R | 1 | unsigned
|  |  | Comm Fault | 2016 | 42017 | R | 1 | unsigned
|  |  | Fault1 | 2017 | 42018 | R | 1 | unsigned
|  |  | Fault2 | 2018 | 42019 | R | 1 | unsigned
|  |  | Warning1 | 2019 | 42020 | R | 1 | unsigned
|  |  | Warning2 | 2020 | 42021 | R | 1 | unsigned
Analog | % | 10 | Soc | 2026 | 42027 | R | 1 | signed
| % | 10 | Soh | 2027 | 42028 | R | 1 | signed
| V | 10 | DC 전압 | 2028 | 42029 | R | 1 | signed
| A | 100 | DC 전류 | 2029 | 42030 | R | 1 | signed
| kA | 100 | 충전 전류 제한 | 2030 | 42031 | R | 1 | signed
| kA | 100 | 방전 전류 제한 | 2031 | 42032 | R | 1 | signed
| kW | 10 | 충전 전력 제한 | 2032 | 42033 | R | 1 | signed
| kW | 10 | 방전 전력 제한 | 2033 | 42034 | R | 1 | signed
| V | 10 | 최대 CELL 전압 | 2034 | 42035 | R | 1 | signed
| V | 10 | 최소 CELL 전압 | 2035 | 42036 | R | 1 | signed
|  | 10 | 최대 모듈 온도 | 2036 | 42037 | R | 1 | signed
|  | 10 | 최소 모듈 온도 | 2037 | 42038 | R | 1 | signed
|  | 10 | 컨테이너 온도 | 2038 | 42039 | R | 1 | signed
|  |  | RelayClose | 2039 | 42040 | R | 1 | signed
|  |  | Reserved | 2040 | 42041 | R | 1 | signed

## PCS 제어코드
DEC | BIT
1 | 0x01 | RUN
2 | 0x02 | STOP
4 | 0x03 | STAND BY
8 | 0x04 | CHARGE
16 | 0x05 | DISCHARGE
32 | 0x06 | EMERGENCY
64 | 0x07 | RESET
128 | 0x08 | RELAY_CLOSE
256 | 0x09 | RELAY_OPEN
512 | 0x10 | BSC_EVENT_CLEAR
1024 | 0x11 | BSC_RESTART
2048 | 0x12 | ISOLATION
4096 | 0x13 | STOP_ISOLATION
8192 | 0x14 | HEART_BEAT
16384 | 0x15 | FR_CHARGE
32768 | 0x16 | FR_DISCHARGE